November 21, 1997

Contract # TW-0928

SPECIAL SPECIFICATION

SECTION 11470 -S

DARKROOM EQUIPMENT

Page

PART 1 - GENERAL

1.01	Summary	2

1.02	Submittals	2

1.03	Quality Assurance	3

1.04	Delivery, Storage, and Handling	3

1.05	Project Conditions	3

1.06	Warranty	3

PART 2 - PRODUCTS

2.01	Manufacturers/Suppliers	4

2.02	Processing Sinks 	4

2.03	Safelights	5

2.04	Illuminated Sign	5

2.05	Rotary Darkroom Door	6

2.06	Lightproof Doorstops	6

2.07	Darkroom Curtain	7

PART 3 - EXECUTION

3.01	Installation	7

3.02	Cleaning and Protection	7

SPECIAL SPECIFICATION

SECTION 11470-S

DARKROOM EQUIPMENT

THIS SECTION USES THE TERM "ARCHITECT."  CHANGE THIS TERM AS NECESSARY TO MATCH THE ACTUAL TERM USED TO IDENTIFY DESIGN PROFESSIONAL AS DEFINED IN THE GENERAL AND SUPPLEMENTARY CONDITIONS.

PART 1 - GENERAL

1.01	SUMMARY

A.	Section Includes:

1.	Sinks and Fittings

2.	Safelights

3.	Illuminated Sign

4.	Rotary Darkroom Doors

5.	Lightproof Doorstops

6.	Darkroom Curtains

B.	Related Sections:

1.	Division 15:  Furnishing and installation of plumbing utilities and final connections to service fittings.

2.	Division 16:  Furnishing and installation of electrical utilities and final connections to equipment.

1.02	SUBMITTALS

A.	Product Data:  Submit manufacturer's data for each item of darkroom equipment specified. Include component dimensions, configurations, construction details, joint details, and utility service requirements and locations.

B.	Shop Drawings:

1.	Provide 3/4 inch = 1'-0" scale elevations of individual casework units, cross sections, rough-in and anchor placements, tolerances and clearances. Indicate relation of units to surrounding walls, doors and other building components.

2.	Provide 1/4 inch = 1'-0" rough-in plan drawings for coordination with trades.

3.	Provide 1 set of sepia reproducible prints and 1 set of blueline prints.

C.	Submit the above in accordance with section 1300-S.

1.03	QUALITY ASSURANCE

A.	Single Source Responsibility:  Casework, work surfaces, darkroom equipment and accessories manufactured or furnished by a single darkroom equipment supplier.

B.	Manufacturer's Qualifications:  5 years or more experience in the manufacture of darkroom equipment of type specified.

1.04	DELIVERY, STORAGE, AND HANDLING

A.	Ship equipment in sections, as required, to allow the largest components to fit through a standard 3'-0" by 6'-8" door.

B.	Store equipment in a clean, dry location, protected against damage of any kind. Cover with tarpaulin or polyethylene sheeting. Allow for air circulation inside the covering.

C.	Protect all work surfaces throughout construction period with 1/4 inch corrugated cardboard completely covering the top and securely taped to edges.

1.05	PROJECT CONDITIONS

A.	Do not deliver or install equipment until the following conditions have been met:

1.	Building areas are dry and unexposed to adverse weather conditions which may damage finished materials.

2.	Interior building temperatures are above 65 degrees Fahrenheit in areas of casework and equipment installation to permit the proper curing of epoxy sealants and adhesives.

1.06	WARRANTY

A.	Provide a 1 year warranty against defects in materials and workmanship.

PART 2   PRODUCTS

2.01	MANUFACTURERS/SUPPLIERS

A.	Kreonite, Inc.

P.O. Box 2099

Wichita, Kansas 67201

(316) 263-1111

B.	Leedal, Inc.

1918 South Prairie Avenue

Chicago, Illinois  60616

(312) 842-6588

C.	Photolab Innovations

3328 Monte Carlo Court

Lancaster, California  93536

(805) 722-3170

D.	Photo Lab Fabrications

159 Brightside Avenue

Central Islip, New York  11722

(800) 422-0101

E.	Kreonite, Inc. or Photo Lab Fabrications Model Numbers are indicated on the Drawings.

Substitutions: only under provisions of Section 1600-S.

2.02	PROCESSING SINKS

A.	Manufacturer:  Kreonite Model Number 2465E2C.

B.	Construction:  Each sink unit completely assembled at the factory and consisting of the sink, base cabinet, and prepiped fittings and equipment. Base cabinets as described for darkroom casework.

C.	Sink Materials and Fabrication:  Fabricated with a polyester resin work surface, reinforced with a glass fiber mat. Work surface resistant to the corrosive effects of chemicals required in photographic and graphic arts processing. One piece molded construction with radius inside and outside corners and bottom sloped to ensure positive drainage.

D.	Fittings:  Provide units with the following equipment and fittings factory mounted and prepiped:

1.	Water temperature blender:  Kreonite Model KTB251; jet inlets, blended water valve, jet control, vacuum breaker, and thermometer.

2.	Faucet:  Kreonite Model KF220S; hot water valve, cold water valve, and spray hose.

3.	Water filter:  Kreonite Model KWF600; 25 micron, blended water only.

4.	Faucet:  Kreonite Model KFC110VB; single valve, vacuum breaker.

5.	Spout end:  Kreonite Model KSE3; for hose attachment for blended and filtered water from KTB250 blender.

6.	Standpipe and basket strainer; Kreonite Model KSP1; 1 inch size.

7.	Provide 1/2 inch hot water, 1/2 inch cold water, and 1-1/2 inch drain connections.

8.	Plumbing equipment package shall provide filtered water at all fixtures.

E.	Chiller:  Provide each sink unit with factory installed water chiller; Kreonite Model KR100-IN. Chiller installation shall include piping and changeover valves. Electrical requirements:  1 horsepower, 5.8 amps, 208/60/1.

2.03	SAFELIGHTS

A.	Thomas Duplex safelights, Type DUB for black and white printing.

B.	Provide unit with 3 available levels of illumination and built-in filter with adjustable louvers to hold added filters. Soft orange-yellow light from quartz sodium-vapor discharge tube.

C.	Mounting:  Suspended from ceiling to provide indirect lighting.

D.	Electrical:  35 watts, 120/60/1. Provide with a 3 wire grounding plug to plug into a ceiling mounted outlet.

2.04	ILLUMINATED SIGN

A.	Type:  Wall mounted to read "DARKROOM IN USE" when illuminated.

B.	Size:  12 inches wide by 3 inches deep by 8 inches high.

C.	Electrical:  210 watts; 2.5 amps; 120/60/1.

2.05	ROTARY DARKROOM DOOR

A.	Size:

Kreonite	Door		Door		Opening      	Opening

Type	Model No.	Width		Height		Width		Height

2-Way	KRD 36-2W	35" 		82-1/4"	36		80"

B.	Construction

1.	Rigid high-impact petroleum hydrocarbon polystyrene.

2.	Steel structural members.

3.	Reinforced steel flanges around the outside.

4.	Breakaway aluminum flange bolted to a steel mounting flange.

C.	Features:

1.	Rotation from inside and outside.

2.	Suspension and lower guide bearings.

3.	Wrap around aluminum handrail.

4.	Finger grips around the outside.

5.	Security lock.

6.	Breakaway hardware.

2.06	LIGHTPROOF DOORSTOPS

A.	Manufacturer:  Kreonite, Inc. Model PLFLTK with Number 485 perimeter door seal and Number 361 sill protection.

B.	Perimeter Door Seal:  Extruded aluminum housing with a solid neoprene plunger.

C.	Sill Protection:  Drop seal constructed of closed cell sponge neoprene with an extruded aluminum housing.

D.	Devices to operate automatically and be weatherproof, lightproof and soundproof.

2.07	DARKROOM CURTAIN

A.	Curtain Material:  Composed of 34 percent SEF modacrylic, 32 percent Saran flat monofilament and 34 percent viscose rayon; double-vinyl laminated back for opacity. The material to be inherently and permanently flame resistant and pass the flame resistance requirements in accordance with NFPA Standard Number 701.

B.	Panels:  Sew flat with 10 percent fullness. Seams sewn with no raw edges. Curtain top to be grommeted on 8 inch centers and bottom edge weighted and overlap with floor. Outside vertical edges provided with Velcro quick seal strips to facilitate light trap overlaps and easy attachment to walls.

C.	Valances:  Provide with front and rear light trap valances. The valances made of the same blackout curtain material, sewn with pleats, with a sewn-on Velcro strip, and mounted to the curtain track assembly using the light trap interface.

D.	Curtain Track:  Constructed of satin anodized aluminum designed for surface mounting to the underside of the ceiling. Extruded aluminum box-channel 1-3/8 inches by 3/4 inch, slotted on the underside to receive 2-wheeled carriers. The track to serve as an integral part of the valance assembly. Fastening not more than 3'-0" on centers. Corners to be 1 piece, 12 inch radius, 90 degrees track sections. Provide with hook carriers, end caps, snap-outs, and connectors.

PART 3   EXECUTION

3.01	INSTALLATION

A.	Deliver to job site, uncrate, place in location, and assemble all equipment specified herein. Remove all debris and crating materials.

B.	Install laboratory darkroom equipment in strict accordance with the manufacturer's recommendations, including recommended operating and servicing clearances.

C.	Mechanical Hookups:  Under Division 15.

D.	Electrical Hookups:  Under Division 16.

3.02	CLEANING AND PROTECTION

A.	Repair or remove and replace defective work upon completion of installation.

B.	Clean equipment, touch up as required, and remove and refinish damaged or soiled areas.

C.	Cover equipment for protection against soiling and deterioration during remainder of construction period.

D.	Clean equipment as recommended by the manufacturer and leave free of all grease and streaks. Use no wax or oils.

E.	Protect equipment before, during, and after installation. Materials damaged due to improper protection shall be cause for rejection.

END OF SECTION